## System data
Base power | 10 MVA
Base voltage | 12.66 kV
Upper bound for voltage | 1.07 p.u.
Lower bound for voltage | 0.93 p.u.
Planning horizon | 5 years
Discount rate | 10%
Annual load growth | 3%
Per-unit cost of electricity purchase | 0.5 ¥/kWh
Per-unit cost of PV curtailment | 5 ¥/kWh
Per-unit cost of load shedding | 50 ¥/kWh
Optimal gap of Benders decomposition algorithm | 0.01%

## Feeder data
Existing feeders |  |  |  | Candidate feeders
From | To | Resistance (Ω) | Reactance (Ω) | From | To | Length (km)
1 | 2 | 0.0922 | 0.047 | 19 | 34 | 0.62
2 | 3 | 0.493 | 0.2511 | 34 | 35 | 0.58
3 | 4 | 0.366 | 0.1864 | 35 | 36 | 0.75
4 | 5 | 0.3811 | 0.1941 | 36 | 37 | 0.42
5 | 6 | 0.819 | 0.707 | 37 | 38 | 0.83
6 | 7 | 0.1872 | 0.6188 | 38 | 39 | 0.78
7 | 8 | 0.7114 | 0.2351 | 39 | 40 | 0.72
8 | 9 | 1.03 | 0.74 | 21 | 34 | 1.36
9 | 10 | 1.044 | 0.74 | 7 | 35 | 1.72
10 | 11 | 0.1966 | 0.065 | 9 | 38 | 1.32
11 | 12 | 0.3744 | 0.1238 | 11 | 40 | 1.25
12 | 13 | 1.468 | 1.155 | 35 | 39 | 0.8
13 | 14 | 0.5416 | 0.7129
14 | 15 | 0.591 | 0.526
15 | 16 | 0.7463 | 0.545
16 | 17 | 1.289 | 1.721
17 | 18 | 0.732 | 0.574
2 | 19 | 0.164 | 0.1565
19 | 20 | 1.5042 | 1.3554
20 | 21 | 0.4095 | 0.4784
21 | 22 | 0.7089 | 0.9373
3 | 23 | 0.4512 | 0.3083
23 | 24 | 0.898 | 0.7091
24 | 25 | 0.896 | 0.7011
6 | 26 | 0.203 | 0.1034
26 | 27 | 0.2842 | 0.1447
27 | 28 | 1.059 | 0.9337
28 | 29 | 0.8042 | 0.7006
29 | 30 | 0.5075 | 0.2585
30 | 31 | 0.9744 | 0.963
31 | 32 | 0.3105 | 0.3619
32 | 33 | 0.341 | 0.5302

## Node data
Existing nodes |  |  | New nodes
Number | Active load (kW) | Reactive load (kVar) | Number | Active load (kW) | Reactive load (kVar) | PV capacity (kW) | Connected year
1 | 0 | 0 | 34 | 150 | 70 | 1000 | 1
2 | 100 | 60 | 35 | 120 | 60 | 1000 | 1
3 | 90 | 40 | 36 | 80 | 30 | 1000 | 1
4 | 120 | 80 | 37 | 80 | 30 | 600 | 2
5 | 60 | 30 | 38 | 80 | 30 | 600 | 2
6 | 60 | 20 | 39 | 60 | 20 | 600 | 3
7 | 200 | 100 | 40 | 60 | 20 | 600 | 3
8 | 200 | 100
9 | 60 | 20
10 | 60 | 20
11 | 45 | 30
12 | 60 | 35
13 | 60 | 35
14 | 120 | 80
15 | 60 | 10
16 | 60 | 20
17 | 60 | 20
18 | 90 | 40
19 | 90 | 40
20 | 90 | 40
21 | 90 | 40
22 | 90 | 40
23 | 90 | 50
24 | 420 | 200
25 | 420 | 200
26 | 60 | 25
27 | 60 | 25
28 | 60 | 20
29 | 120 | 70
30 | 200 | 600
31 | 150 | 70
32 | 210 | 100
33 | 60 | 40

## Cable data
Common parameters
Installation cost of DTR equipment | 50000 ¥
Design lifetime | 30 years
Maximum temperature limit of hot-spot temperature | 90 ℃
Cable type | Three Core Aluminium Conductor XLPE Insulated Steel Wire Armoured
Thermal resistivity of insulation | 3.5 K∙m/W
Thermal resistivity of jacket | 6 K∙m/W
Special heat of conductor | 2.5*106 J/m3∙K
Special heat of insulation | 2.4*106 J/m3∙K
Special heat of screen | 3.45*106 J/m3∙K
Special heat of armour | 3.8*106 J/m3∙K
Special heat of jacket | 1.7*106 J/m3∙K
Soil textural classes | Clay loams
Candidate cable types | Type 1 | Type 2 | Type 3
Rated current (A) | 100 | 185 | 320
Construction cost (¥/km) | 300000 | 500000 | 700000
Replacement cost (¥/km) | - | 450000 | 600000
Resistance per-unit length (Ω/km) | 1.2 | 0.443 | 0.16
Reactance per-unit length (Ω/km) | 0.127 | 0.107 | 0.097
Loss factor of screen | 0.0019 | 0.0062 | 0.021
Nominal cross-section of conductor (mm2) | 25 | 70 | 185
Diameter of conductor (mm) | 5.6 | 9.4 | 16
Thickness of insulation (mm) | 4.5 | 4.5 | 4.5
Thickness of screen (mm) | 0.2 | 0.2 | 0.2
Thickness of inner coverings and fillers (mm) | 1.4 | 1.5 | 1.8
Thickness of armour (mm) | 0.5 | 0.5 | 0.5
Thickness of jacket (mm) | 2.5 | 2.8 | 3.3

## Transformer data
Common parameters
Installation cost of DTR equipment | 10000 ¥
Design lifetime | 30 years
Top-oil rise over ambient temperature at rated load | 55 ℃
Winding hot-spot rise over top-oil temperature at rated load | 25 ℃
Oil time constant | 155 min
Winding time constant | 5 min
Ratio of load loss at rated load to no-load loss | 8
Maximum temperature limit of hot-spot temperature | 120 ℃
Candidate transformer types | Type 1 | Type 2 | Type 3
Rated capacity (kVA) | 400 | 600 | 1000
Construction cost (¥) | 80000 | 110000 | 150000

## Scenario data
Probability of scenarios (%)
| Scenario 1 | Scenario 2 | Scenario 3 | Scenario 4 | Scenario 5 | Scenario 6 | Scenario 7 | Scenario 8
| 7.9452 | 16.9863 | 6.0274 | 12.6027 | 9.0411 | 10.137 | 22.7397 | 14.5205
Load demand factor (p.u.)
Time (h) | Scenario 1 | Scenario 2 | Scenario 3 | Scenario 4 | Scenario 5 | Scenario 6 | Scenario 7 | Scenario 8
1 | 0.58738 | 0.51711 | 0.4864 | 0.48851 | 0.52229 | 0.53612 | 0.55985 | 0.51816
2 | 0.56165 | 0.49583 | 0.46493 | 0.45549 | 0.4992 | 0.50438 | 0.52761 | 0.49432
3 | 0.5357 | 0.47874 | 0.44499 | 0.43199 | 0.48393 | 0.46024 | 0.4999 | 0.47795
4 | 0.52041 | 0.46963 | 0.43672 | 0.41324 | 0.47908 | 0.44081 | 0.47219 | 0.47223
5 | 0.53167 | 0.47719 | 0.44941 | 0.4405 | 0.47443 | 0.46727 | 0.458 | 0.49038
6 | 0.55466 | 0.51054 | 0.47509 | 0.50489 | 0.4791 | 0.52 | 0.47505 | 0.51913
7 | 0.64986 | 0.59727 | 0.54655 | 0.58373 | 0.50141 | 0.62835 | 0.55275 | 0.60656
8 | 0.75659 | 0.70017 | 0.64013 | 0.67138 | 0.53939 | 0.71166 | 0.64117 | 0.71917
9 | 0.79407 | 0.69644 | 0.67022 | 0.72167 | 0.58064 | 0.70397 | 0.69029 | 0.73885
10 | 0.79496 | 0.71045 | 0.6879 | 0.73589 | 0.60389 | 0.7257 | 0.70999 | 0.78411
11 | 0.82333 | 0.74884 | 0.71284 | 0.74612 | 0.6244 | 0.73546 | 0.72171 | 0.79892
12 | 0.85662 | 0.78822 | 0.7342 | 0.76236 | 0.62764 | 0.77859 | 0.71112 | 0.81705
13 | 0.86991 | 0.79437 | 0.74633 | 0.7678 | 0.62805 | 0.78794 | 0.71642 | 0.82853
14 | 0.88405 | 0.79115 | 0.74624 | 0.77441 | 0.62712 | 0.78604 | 0.71543 | 0.82234
15 | 0.88623 | 0.77348 | 0.74751 | 0.77759 | 0.63045 | 0.78032 | 0.7239 | 0.81332
16 | 0.88124 | 0.76371 | 0.74499 | 0.76925 | 0.6312 | 0.76656 | 0.73561 | 0.81447
17 | 0.87925 | 0.75759 | 0.73339 | 0.76151 | 0.60496 | 0.76947 | 0.77291 | 0.78854
18 | 0.85567 | 0.7495 | 0.70857 | 0.75598 | 0.61241 | 0.79766 | 0.8212 | 0.76535
19 | 0.79011 | 0.72999 | 0.65288 | 0.74918 | 0.6049 | 0.80612 | 0.80722 | 0.72192
20 | 0.72746 | 0.71411 | 0.63621 | 0.71456 | 0.59564 | 0.7817 | 0.78076 | 0.69053
21 | 0.69551 | 0.68071 | 0.5962 | 0.66286 | 0.59554 | 0.72235 | 0.74408 | 0.65672
22 | 0.65049 | 0.60362 | 0.5563 | 0.6098 | 0.58016 | 0.66541 | 0.69603 | 0.60574
23 | 0.6246 | 0.52539 | 0.51786 | 0.58824 | 0.56254 | 0.63716 | 0.63998 | 0.55976
24 | 0.62022 | 0.55609 | 0.51673 | 0.54266 | 0.54015 | 0.58309 | 0.59083 | 0.5642
PV output factor (p.u.)
Time (h) | Scenario 1 | Scenario 2 | Scenario 3 | Scenario 4 | Scenario 5 | Scenario 6 | Scenario 7 | Scenario 8
1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 0 | 0 | 0 | 0 | 0.0028691 | 0 | 0 | 0
6 | 0.041175 | 0.048012 | 0 | 0 | 0.072897 | 0 | 0 | 0.0028322
7 | 0.19145 | 0.22219 | 0.034868 | 0.017977 | 0.18265 | 0.010177 | 0 | 0.068996
8 | 0.39627 | 0.40044 | 0.17799 | 0.15214 | 0.36927 | 0.14211 | 0.059889 | 0.22293
9 | 0.49723 | 0.40598 | 0.31013 | 0.29607 | 0.47855 | 0.33248 | 0.18488 | 0.35419
10 | 0.71596 | 0.51375 | 0.44317 | 0.50208 | 0.55518 | 0.48783 | 0.33018 | 0.45489
11 | 0.83125 | 0.57685 | 0.4379 | 0.61914 | 0.6773 | 0.58716 | 0.44465 | 0.57773
12 | 0.86385 | 0.49968 | 0.61072 | 0.6654 | 0.7317 | 0.58561 | 0.46634 | 0.61531
13 | 0.80451 | 0.67933 | 0.57223 | 0.66024 | 0.73812 | 0.55726 | 0.40308 | 0.52133
14 | 0.76205 | 0.54616 | 0.57163 | 0.60016 | 0.66215 | 0.55252 | 0.29847 | 0.4975
15 | 0.64097 | 0.45512 | 0.45997 | 0.4879 | 0.48481 | 0.43965 | 0.21699 | 0.4415
16 | 0.55552 | 0.32772 | 0.33271 | 0.32945 | 0.36554 | 0.27471 | 0.1328 | 0.30567
17 | 0.34808 | 0.23958 | 0.19022 | 0.14413 | 0.31254 | 0.13168 | 0.027452 | 0.093691
18 | 0.1886 | 0.080393 | 0.037469 | 0.0090206 | 0.18714 | 0.0089916 | 0 | 0.074538
19 | 0.072095 | 0.0017211 | 0 | 0 | 0.038959 | 0 | 0 | 0.0093348
20 | 0.00013886 | 0 | 0 | 0 | 0 | 0 | 0 | 0
21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ambient air temperature (℃)
Time (h) | Scenario 1 | Scenario 2 | Scenario 3 | Scenario 4 | Scenario 5 | Scenario 6 | Scenario 7 | Scenario 8
1 | 21.1571 | 15.0086 | 18.2444 | 13.8601 | 18.0426 | 12.5713 | 12.5244 | 18.5285
2 | 20.9004 | 14.6934 | 18.2209 | 13.1519 | 17.8133 | 12.1151 | 12.5464 | 18.31
3 | 20.643 | 14.5491 | 18.1413 | 12.7475 | 17.5659 | 11.7917 | 13.047 | 18.239
4 | 20.4228 | 14.4063 | 18.0355 | 12.4329 | 17.5635 | 11.5692 | 13.1573 | 18.1644
5 | 20.713 | 14.3619 | 17.8102 | 11.7467 | 17.1972 | 10.8436 | 12.5287 | 18.0278
6 | 20.9299 | 14.7307 | 17.4825 | 11.978 | 17.7574 | 10.5341 | 12.3625 | 18.0127
7 | 21.8664 | 15.9319 | 17.7968 | 12.1433 | 18.6162 | 10.5231 | 12.1853 | 18.2926
8 | 23.2632 | 17.0219 | 18.9905 | 13.1723 | 19.4292 | 11.6475 | 12.5096 | 19.0805
9 | 24.4264 | 17.7651 | 20.1185 | 15.1518 | 20.1069 | 13.5867 | 13.1745 | 19.8905
10 | 26.0411 | 18.4911 | 21.1501 | 17.364 | 20.4752 | 15.4366 | 13.7878 | 20.5322
11 | 27.3951 | 18.9788 | 21.6157 | 18.9316 | 20.8783 | 17.2435 | 14.5673 | 21.0721
12 | 28.491 | 18.9367 | 22.3511 | 19.9243 | 21.1616 | 17.8635 | 15.3272 | 21.4299
13 | 29.1561 | 19.3451 | 22.6393 | 20.6065 | 21.2542 | 17.6848 | 15.7977 | 21.6418
14 | 29.5584 | 18.9678 | 22.7729 | 21.0477 | 21.1353 | 17.7316 | 15.9606 | 21.7258
15 | 29.1792 | 18.6392 | 22.7324 | 21.2043 | 20.7508 | 17.5568 | 15.6754 | 21.7747
16 | 28.7363 | 18.3683 | 22.4853 | 20.9824 | 20.4203 | 16.8151 | 15.1963 | 20.9048
17 | 25.8055 | 18.0459 | 22.3755 | 20.1794 | 20.5655 | 15.6797 | 14.8424 | 21.4902
18 | 24.9941 | 17.5974 | 21.5695 | 18.9051 | 20.2082 | 14.5047 | 14.4684 | 21.6579
19 | 23.7014 | 17.2726 | 20.8398 | 18.4596 | 19.8151 | 13.7653 | 14.3051 | 21.515
20 | 22.5469 | 17.0825 | 20.4097 | 18.3558 | 19.411 | 13.303 | 14.2277 | 21.0644
21 | 22.079 | 16.5428 | 19.9946 | 18.2624 | 19.1727 | 13.1019 | 14.1241 | 20.5573
22 | 21.8738 | 16.0852 | 19.2854 | 17.3513 | 19.1851 | 12.9233 | 14.0858 | 20.6681
23 | 21.4909 | 15.8646 | 18.4522 | 15.6707 | 18.9023 | 12.6161 | 14.1938 | 20.6731
24 | 21.1869 | 15.7375 | 18.3582 | 14.635 | 18.7796 | 12.2555 | 14.2382 | 20.572
Ambient soil temperature (℃)
Time (h) | Scenario 1 | Scenario 2 | Scenario 3 | Scenario 4 | Scenario 5 | Scenario 6 | Scenario 7 | Scenario 8
1 | 21.7733 | 17.6615 | 20.7846 | 19.4459 | 21.3685 | 14.3667 | 15.2497 | 22.361
2 | 21.7819 | 17.6505 | 20.7807 | 19.4357 | 21.3593 | 14.3656 | 15.244 | 22.3512
3 | 21.7904 | 17.6393 | 20.7768 | 19.4254 | 21.352 | 14.3651 | 15.2402 | 22.3395
4 | 21.7971 | 17.6281 | 20.7706 | 19.4137 | 21.3427 | 14.3627 | 15.2365 | 22.3278
5 | 21.8019 | 17.6151 | 20.7629 | 19.401 | 21.3334 | 14.3585 | 15.2307 | 22.3177
6 | 21.8066 | 17.6019 | 20.7567 | 19.3854 | 21.3222 | 14.3529 | 15.225 | 22.3061
7 | 21.8092 | 17.589 | 20.7487 | 19.3697 | 21.3126 | 14.3454 | 15.2192 | 22.2924
8 | 21.8141 | 17.5778 | 20.7404 | 19.3546 | 21.3034 | 14.34 | 15.2133 | 22.2807
9 | 21.8188 | 17.5688 | 20.7343 | 19.3412 | 21.2922 | 14.3349 | 15.2075 | 22.2668
10 | 21.8253 | 17.5594 | 20.7279 | 19.3281 | 21.2827 | 14.3278 | 15.2018 | 22.257
11 | 21.8341 | 17.5543 | 20.7235 | 19.3168 | 21.273 | 14.3251 | 15.1978 | 22.247
12 | 21.8446 | 17.5509 | 20.7228 | 19.3097 | 21.2675 | 14.3243 | 15.196 | 22.2372
13 | 21.8573 | 17.5497 | 20.724 | 19.3027 | 21.2621 | 14.3256 | 15.196 | 22.2311
14 | 21.8717 | 17.5502 | 20.7253 | 19.2995 | 21.2584 | 14.3292 | 15.196 | 22.2253
15 | 21.8883 | 17.5526 | 20.7284 | 19.3002 | 21.2526 | 14.3326 | 15.196 | 22.223
16 | 21.9047 | 17.5551 | 20.7355 | 19.2992 | 21.2509 | 14.3386 | 15.1978 | 22.2189
17 | 21.9252 | 17.5592 | 20.7404 | 19.3002 | 21.2492 | 14.3441 | 15.1998 | 22.2167
18 | 21.9438 | 17.5639 | 20.7472 | 19.3031 | 21.2455 | 14.35 | 15.2038 | 22.2126
19 | 21.9604 | 17.566 | 20.7521 | 19.3043 | 21.2417 | 14.3558 | 15.2058 | 22.2084
20 | 21.9789 | 17.5685 | 20.7567 | 19.3053 | 21.2401 | 14.3601 | 15.2075 | 22.2064
21 | 21.9938 | 17.5688 | 20.7616 | 19.3066 | 21.2365 | 14.3632 | 15.2093 | 22.2023
22 | 22.0084 | 17.5692 | 20.7643 | 19.3058 | 21.2328 | 14.3651 | 15.211 | 22.1981
23 | 22.0214 | 17.5675 | 20.765 | 19.3051 | 21.2274 | 14.3653 | 15.211 | 22.194
24 | 22.0343 | 17.566 | 20.7658 | 19.3024 | 21.2237 | 14.3653 | 15.2127 | 22.1881
Soil moisture content (m3/m3)
Time (h) | Scenario 1 | Scenario 2 | Scenario 3 | Scenario 4 | Scenario 5 | Scenario 6 | Scenario 7 | Scenario 8
1 | 0.18995 | 0.1926 | 0.27607 | 0.23142 | 0.1837 | 0.27109 | 0.23985 | 0.16866
2 | 0.18995 | 0.19286 | 0.27595 | 0.23138 | 0.18367 | 0.27102 | 0.23984 | 0.16866
3 | 0.18995 | 0.19312 | 0.27582 | 0.23134 | 0.18365 | 0.27096 | 0.23981 | 0.16866
4 | 0.18993 | 0.19336 | 0.27569 | 0.23128 | 0.18364 | 0.27092 | 0.23979 | 0.16868
5 | 0.18993 | 0.19361 | 0.27556 | 0.23125 | 0.18362 | 0.27087 | 0.23977 | 0.16868
6 | 0.18991 | 0.19385 | 0.27543 | 0.2312 | 0.18359 | 0.27081 | 0.23976 | 0.16868
7 | 0.18988 | 0.19406 | 0.27531 | 0.23115 | 0.18356 | 0.27076 | 0.23973 | 0.16868
8 | 0.18984 | 0.19425 | 0.27518 | 0.23108 | 0.18349 | 0.27071 | 0.23971 | 0.16868
9 | 0.18973 | 0.19441 | 0.27501 | 0.23102 | 0.1834 | 0.27061 | 0.23968 | 0.16866
10 | 0.18959 | 0.19455 | 0.27482 | 0.23088 | 0.1833 | 0.27049 | 0.23964 | 0.16863
11 | 0.18942 | 0.19469 | 0.27463 | 0.23073 | 0.18317 | 0.27035 | 0.23958 | 0.16857
12 | 0.18923 | 0.19481 | 0.27436 | 0.23054 | 0.18302 | 0.27017 | 0.2395 | 0.16852
13 | 0.18903 | 0.19492 | 0.27412 | 0.23035 | 0.18286 | 0.27002 | 0.23942 | 0.16849
14 | 0.18883 | 0.19504 | 0.27388 | 0.23016 | 0.18272 | 0.26986 | 0.23938 | 0.16845
15 | 0.18868 | 0.19516 | 0.27366 | 0.23001 | 0.1826 | 0.26971 | 0.23932 | 0.16842
16 | 0.18856 | 0.19528 | 0.27347 | 0.22987 | 0.18251 | 0.26961 | 0.23929 | 0.16838
17 | 0.18849 | 0.19542 | 0.2733 | 0.22981 | 0.18244 | 0.26951 | 0.23927 | 0.16838
18 | 0.18848 | 0.19556 | 0.27318 | 0.22975 | 0.18239 | 0.26947 | 0.23927 | 0.16838
19 | 0.18847 | 0.19571 | 0.27305 | 0.22971 | 0.18236 | 0.26941 | 0.23926 | 0.16838
20 | 0.18845 | 0.19586 | 0.27293 | 0.22966 | 0.18234 | 0.26933 | 0.23924 | 0.16838
21 | 0.18843 | 0.196 | 0.27281 | 0.22961 | 0.18233 | 0.26928 | 0.23923 | 0.16838
22 | 0.18843 | 0.19614 | 0.2727 | 0.22957 | 0.18231 | 0.26923 | 0.23923 | 0.16838
23 | 0.18843 | 0.19629 | 0.27258 | 0.22952 | 0.1823 | 0.26916 | 0.23923 | 0.1684
24 | 0.18842 | 0.19643 | 0.27247 | 0.22948 | 0.18228 | 0.26912 | 0.23921 | 0.1684